SCOPE OF SERVICE

DOMESTIC HOT WATER BOILER SYSTEM INSPECTION AND TESTING

The scope of service includes twice yearly inspections of existing domestic water heating boiler(s) and related components and equipment.  A written report, indicating items inspected, existing conditions and recommendations is to be provided to the Property Manager immediately upon completion of the inspection.  Life safety or code compliance issues are to be brought to the immediate attention of the Property Manager.

Inspection Criteria

- Inspect boiler and storage tank controls, to include but not be limited to: all safety, monitoring, operating and limit controls and switch(es), thermostatic controls, and all other devices.  Inspect and reset, as necessary, temperature settings to insure safe supply water temperatures are maintained. Record data on service ticket.

- Inspect and adjust to manufacturer’s specification, as necessary, the manifold gas pressure supplying the boiler(s). Record pressure setting.

- Inspect all sources of combustion air for freedom of air movement.  Remove any obstructions possible.  List deficiencies on work order and immediately notify Property Management of any obstructions beyond the technician’s ability to remove, as well as any non-boiler related storage or other unauthorized items in the room.

- Inspect temperature and pressure relief valves for signs of leakage. Record findings.

- Inspect the ventilation ductwork inside and outside of boiler room.

- Inspect the condition of the refractory and burners. Record findings.

- Take appropriate temperature readings to insure temperature rise across heat exchanger is within manufacturer’s specifications. Record findings. Visually inspect heat exchanger, as well as outside of boiler, for signs of overheating, leaks, etc.

- Inspect circulation and system pumps for correct operation.  Check voltage and amperage readings of each motor and check against manufacturer’s nameplate ratings. Record compliance within manufacturer’s operating limits.

- Lubricate all pumps, components and motors per manufacturer’s specifications.

- Replace any component covers removed for inspection purposes and return system to normal operation, observing system to insure correct operation prior to completion of inspection.

- If a remote device is used to control system operation, inspect temperature settings to insure safe supply water temperatures are maintained.  Inspect device for correct operation per manufacturer’s specifications.

- Inspect storage tank(s) and fittings for leaks. Note any pipe leaks or fitting leaks observed in the boiler room.

- Verify that thermometers on the hot water supply lines and return lines are accurate within a tolerance of + 3 degrees F. Report defective devices on work tickets.

Follow-up with the property staff on the findings from the inspections and provide a written proposals for correcting any deficiencies found during the inspection process.