CHIMNEY AND DRYER VENT CLEANING

SCOPE OF WORK

Thoroughly sweep chimneys to remove soot build-up and debris in the chimney flue.

Clean and remove lint, dust and any debris, which could cause obstructions in the dryer vent stack.  Inspect vent openings at roof or walls to ensure sufficient draft.  Remove damper doors at roof or wall opening, if allowed by code, and place hardware screen over stack to prevent birds and other creatures from infiltrating the dryer vents.

Provide permits, materials and labor necessary to sweep designated chimneys.  Inspect dampers and report all problems and concerns to the Property Manager in a written format.

LOCATION

|  | Apartments |
| --- | --- |

DESCRIPTION OF WORK

# General Conditions

Contractor shall obtain a list of apartments to be serviced from the Property Manager.  Work must be performed between 9 a.m. and 4:30 p.m., Monday through Friday.  Prior approval of the Property Manager must be obtained prior to scheduling work at any other time besides the hours listed.

- Remove all tarps, tools and other materials and debris upon completion of work.

- An inspection report noting any problems or concerns should be completed on each cleaned flue and forward to the Property Manager.

- Workers shall be fully clothed at all times in a manner appropriate for weather conditions.  Workers shall not play radios, tapes, etc.   Workers shall use approved restroom facilities only.

# Fireplace Cleaning Requirements

- Flue cap removal and inspection of the flue and cap, bird screening, wind and rain collars, flashing and any apparatus associated with the fireplace chimney.

- Inspection of flue dampers, combustion air vents, firebox, firebox liners, refractories, grates, screens,

doors and hearth.

- Documentation supporting work performed on each chimney shall be submitted at completion of the project. This shall include the level of accumulation, condition of flue, cap, bird screening, wind and rain collars, flashing, flue dampers, combustion air vents, fireboxes, firebox liners, refractories, grates, screens, doors and hearths.

- Place drop cloths in front of the firebox and elsewhere in the apartment as necessary to protect the floor and furniture from becoming soiled or damaged during the cleaning process.

- Inspect and clean the damper.

- Sweep flues using properly sized brushes to remove soot and creosote.  A vacuum shall be connected to the firebox or flue to collect soot as it becomes dislodged.

- Reinstall chimney cap or turbine.

- Reinstall flue cap, bird screening, wind and rain collars, flashing and any other apparatus associated with the fireplace chimney.

- Contractor shall inspect the chimney cap and note any excessive deflection, damaged or split seams, excessive corrosion or loose or missing fasteners in their written report.  Contractor shall be responsible for repairing any damage to the chimney cap that results from their work.

# Dryer Vent Cleaning

- Place drop cloths behind the dryer to prevent lint and dust infiltration into the apartment.

- Using properly sized auger or forced air vacuum system, clean vent piping to insure proper exhaust drafting.

- Remove roof or wall vent trap door and inspect vent opening.  Remove any obstructions found and seal any separations between the duct and vent.

- Install hardware mesh in opening of vent cover, if allowed by code.

- Contractor shall be responsible for repairs to dryer duct work and any other repairs associated with replacement or repair of any duct work damaged or separated as a result of the Contractors work.

Contractor shall notify management immediately of any life threatening conditions.  Contractor shall post a warning notice on the defective equipment until it is repaired.

Contractor is responsible for providing management with a schedule so that appropriate notices may be posted at least one week before project commencement and again 24 hours before commencement.